## 2022
Date Initiated | Building | Project | Owner / Leased | Department / Area | Street | City | Type | Scope of Work | Date SES Onsite | SES Rpt Date | OH&S Consultant Name | OH&S Consultant Rpt Date | Remediator Name | Outcome
2022-05-09 | Gardiner Annex | Exam Div & Susi Office | Leased | DPFR / Exam Division & Mark Susi Office | 76 Northern Ave | Gardiner | Mold | Address water damage & mold issues | NA | NA | AQM | 2022-05-20 | Servpro | Areas successfully remediated
7/5/2022* | Cross State Office Building | HVAC Diffuser Mold | Owned | 4th Flr SOS Area (only) | 111 Sewall St | Augusta | IAQ & Mold | Remediate areas / issues based on AQM report | NA | NA | AQM | 2022-06-06 | Servpro | Diffusers and ceiling tiles cleaned and flex-ducts replaced
2022-06-30 | 221 State St | Idexx Break Rm 063022 | Owned | HETL - Idexx Break Rm | 221 State St | Augusta | IAQ & Mold, Asbestos | Address IAQ complaints; follow-up for asbestos flooring found by AQM | 2022-07-12 | NA | AQM | 2022-07-18 | Atlantic Env | Flooring removed by licensed abatement contractor
7/6/2022* | Cross State Office Building | HVAC Diffuser Mold | Owned | Floors: 1-7 | 111 Sewall St | Augusta | IAQ & Mold | Determine occurrence and extent of mold on diffusers and flex duct | 7/7/2022 - 8/10/22 | 7/11/22 - Flr3, 11/4/22 Flr 1-7 | NA | NA | Servpro | Diffusers and ceiling tiles cleaned throughout the building by Servpro; completed in Dec 2023
2022-07-07 | Cultural Bldg | Library Carpet 070722 | Owned | Library / Flr-2 | 230 State St | Augusta | Mold / Bacteria | Assess carpet for mold contamination following roof leak | 2022-07-08 | 2022-07-12 | None | NA | Servpro | Carpet removed and area cleaned by Servpro
2022-07-14 | Crime Lab | Storage Rms 071422 | Owned | Storage Rooms / Old Drying Lockers | 26 Hospital St | Augusta | Mold | Determine extent and cause of mold growth in Storage Rm / Lockers | 7/15/22, 7/18/22 | 2022-07-20 | AQM | 2022-07-23 | Servpro | Area successuflly remediated and cleaned. PMD asked to replace lower walls that were removed
2022-07-14 | Nash School | Odor 071422 | Owned | 1st and 2nd Floors | 103 Sewall St | Augusta | Odor | Identify source of sewer-like odor | 7/26/22 - 8/2/22 | NA | NA | NA | Building Control | Odor source location narrowed by SES; final ceiling cut by PMD found detached vent pipe; fixed by PMD
2022-07-20 | MFS Ranger Station, Benton | Asbestos 072022 | Owned | Dept of Agriculture, Maine Forest Service | 57 Bangor Rd | Benton | Asbestos | Coordinate asbestos flooring abatement | NA | NA | Atlantic Env | 2022-07-20 | RJ Enterprises | Flooring removed by licensed abatement contractor
7/18/2022* | Gardiner Annex | IAQ 2022 | Leased | DPFR / Whole Building | 76 Northern Ave | Gardiner | Mold, Asbestos | Assess IAQ issues / risks throughout building | 7/20/2022 (Mold), 8/4/22 (Humidity), 8/30/22 (Ceiling) | 7/22/22 (Mold), 8/9/22 (Humidity), 9/8/22 (Ceiling) | AQM | 7/20/2022 (for Landlord), 9/14/22 Carpets | Servpro | All mold and asbestos remediated by summer / fall 2023; Substantial renovations done throughout building to prevent future issues
2022-07-20 | PMD Service Bldg | IAQ 072022 | Owned | BGS Property Management | 15 Columbia St | Augusta | Mold & Asbestos | Employee concern for new work area (general concern due to their own sensitivity) | 2022-07-21 | NA | NA | NA | NA | Employee assignment did not go through; request withdrawn
2022-07-25 | DHHS-Skowhegan | OFI 072522 | Leased | OFI / Old OFI Area | 98 North Ave | Skowhegan | Mold | Assess employee complaints of IAQ concerns / allergy symptoms | 2022-07-27 | 2022-08-02 | AQM | 2022-08-15 | Servpro | All air-supply vents cleaned; all affected areas deep cleaned (by Servpro)
2022-07-25 | Cony Road Building | General Walkthrough | Owned | General | 333 Cony Rd | Augusta | General | Simple participation in walkthrough for any future work requested | 2022-07-26 | NA | NA | NA | NA | SES will assist with any new / future requests
2022-07-27 | CETA | Pre-Renovation Inspection | Owned | All Areas | 27 Indepencence Dr | Augusta | Mold / Lead / Asbestos | Inspection to determine potential exposures to renovation personnel | 2022-08-05 | 2022-08-17 | AQM | 2022-08-17 | NA | Prior reports of lead and asbestos reviewed. BGS & AQM Reports provided to IF&W for their use; BGS role complete
2022-08-05 | 161 Capitol St | Asbestos File Cabinets | Leased | Board of Medicine | 161 Capitol St | Augusta | Asbestos | Remove and dispose of 5 asbestos-containing file cabinets | NA | NA | AQM | 2022-08-22 | Atlantic Env | All cabinets removed by a licensed abatement contractor
2022-08-10 | Cross State Office Building | Mens Room Water Leak | Owned | 1st Flr, 2nd Flr | 111 Sewall St | Augusta | Dryout, Mold | Coordinate drying after water damage and mold remediation in small areas | 2022-08-11 | NA | NA | NA | Servpro | Affected walls either removed or dried in a timely manner; PDM replaced building materials
2022-08-22 | 286 Water St / Key Plaza | 8th & 9th Floors Water Infiltration 2022 | Leased | DHHS / 8th & 9th Floors | 286 Water St | Augusta | Mold | Assess water infiltration (through façade) and possible mold | 8/24/22, 8/31/22, 10/17/22 | 2022-09-12 | Haley Ward | 2023-07-17 | Servpro | Assessment completed by Fall 2023. BGS agreed to remediation scope from Lessor's consultant. Remediation Pending
2022-08-30 | Tyson | Falling Ceiling Paint | Owned | DOC / 3rd Floor | 25 Tyson Dr | Augusta | Lead | Determine if paint falling from ceiling poses a lead-exposure risk | 2022-09-01 | 2022-09-06 | NA | NA | NA | A Full Hazardous Materials Survey was conducted in 1998 by Facility Management Group, Inc. and found no lead in the ceiling paint
2022-08-31 | 286 Water St / Key Plaza | 3rd Floor Cracked Roof Drain | Leased | DHHS / 3rd Floor | 286 Water St | Augusta | Mold | Assess impact to wall system from leak in roof drain | 2022-08-31 | 2022-08-31 | NA | NA | Advance-1 | Remediation successful; PRV test passed
2022-09-01 | Cross State Office Building | Roof Drain Leak | Owned | 5th, 4th and 3rd Floors | 111 Sewall St | Augusta | Mold | Assess impact to walls of columns from leak in roof drain | 2022-09-01 | 2022-09-02 | NA | NA | Servpro | All PRV Tests passed; remediation not needed on 3rd Floor
2022-09-07 | 221 State St | 2nd Floor IAQ | Owned | Areas to be occupied by DPFR | 221 State St | Augusta | IAQ, Mold, Asbestos, Lead | Assess any IAQ concerns prior to occupation by DPFR | 10/4/2022, 10/7/22, 10/11/22 | NA | AQM | 2022-10-19 | Servpro | All relevant areas cleaned; visual inspection revealed well-cleaned surfaces / areas
2022-09-08 | Harlow Bldg | Roof Leak - LUPC | Owned | DACF, 4th Floor Reception in LUPC | 18 Elkins Ln | Augusta | Mold | Assess water impact to ceiling and carpet in Room 413 | 2022-09-09 | NA | AQM | 2022-09-15 | Octagon | All PRV Tests passed
2022-09-19 | 221 State St | Room 114 Sink Leak | Owned | HETL - Shipping & Receiving | 221 State St | Augusta | Mold | Assess damage to sink cabinet | 2022-09-20 | 2022-09-20 | NA | NA | Servpro | Sink dried & isolated, as occupants will be moving out of the building in several weeks
2022-09-29 | Deering | Room 128 Musty Odor | Owned | DOE / Child Nutrition (Room 128) | 90 Blossom Ln | Augusta | Odor (Mold) | Determine source of musty odors | 2022-09-30 | 2022-10-06 | NA | NA | BGS / PMD | PMD will install air-exchanger and set up air-barrier in tunnel to remove / block musty odors
2022-09-29 | 85 Leighton Rd | Printer Toner | Leased | OIT / Print Room | 85 Leighton Rd | Augusta | Chemical / Particulate | Assess surface contamination from printer toner; coordinate cleaning & prevention | 2022-10-07 | 2022-10-17 | NA | NA | Octagon | HVAC system cleaned; All Print Room surfaces / areas detail-cleaned
2022-10-03 | PMD Service Bldg | Dust Concern | Owned | Building Control / Door D10 Entry | 15 Columbia St | Augusta | Asbestos & Lead | Assess concern over dust on floor after drilling into ceiling | 2022-10-03 | NA | NA | NA | NA | No risks present; Building Control notified by email (10/3/22)
2022-10-04 | 10 Water St | Mercury Spill | Leased | Records Center, Warehouse Archives / Records Room | 10 Water St | Hallowell | Mercury | Mercury cleanup in the Records Room | 10/21/22, 10/24/22 | 2022-10-31 | Maine DEP Response | 2022-10-04 | US Ecology | Haley Ward determined that mercury was satisfactorily cleaned and no risks remain
2022-10-06 | Mechanical (CJL) Building | Musty Odor | Owned | 1st Flr Elevator Lobby | 54 Independence Dr | Augusta | Odor (Mold) | Determine cause of odor | NA | NA | NA | NA | NA | Staff reported that adding water to floor traps solved the problem.
2022-10-07 | MFS Ranger Station, Norridgewock | Asbestos Flooring | Owned | All Areas | 564 Skowhegan Rd | Norridgewock | Asbestos | Test flooring for asbestos | NA | NA | AQM | 2022-10-18 | Octagon | All Clearance testing passed
2022-10-07 | CDS-Skowhegan | Odor Complaints | Leased | Entry, Kitchen areas | 16 Madison Ave | Oxford | Odor | Inspect areas with mold odor (Entry) and other odor (Kitchen / general) | 2022-10-12 | 2022-10-25 | NA | NA | NA | No issues in Entry. Rodent issues throughout especially in Kitchen area
2022-10-12 | State House | Attic Sprinkler Leak | Owned | 4th, 3rd, 2nd and 1st Floors | 210 State St | Augusta | Mold | Identify materials still wet following sprinkler leak (10/6/22) | 2022-10-13 | 2022-10-13 | AQM | 2022-11-08 | Servpro | Testing did not reveal any abnormal or concerning mold levels in the affected areas; materials verified as dry
2022-10-13 | MCC-Windham | Asbestos Investigation | Owned | Several Buildings as requested by invloved SOM parties | 17 Mallison Falls Rd | Windham | Asbestos | Re-check roof and windows on several buildings that could not be accessed prior | 2022-10-25 | NA | AQM | 2022-10-30 | Envirovantage | AQM Report received and sent to involved parties
2022-10-17 | Crime Lab | Garage Bay 3 Mold | Owned | Garage Bay 3 | 26 Hospital St | Augusta | Mold | Assess mold on walls in Garage Bay 3 | 10/18/22, 11/1/22 | NA | NA | NA | Octagon | Wall systems remediated and cleaned successfully
2022-10-25 | Cross State Office Building | 6th Floor Roof Leak | Owned | 6th Floor / Attorney General | 111 Sewall St | Augusta | Odor (Mold) | Assesss water impact from ceiling leak at Alma Zachary's cubicle | 2022-10-26 | 2022-10-26 | NA | NA | NA | No significant mold; request submitted to repair roof leak and replace 3 cubicle walls
2022-11-01 | DHHS-Winthrop | Flooring Renovation | Leased | Room 132 (Jordan's Office) | 1705 US Route 202 | Winthrop | Asbestos | Onsite consult for 9x9 floor tiles damaged when pulling up carpet | 2022-11-01 | NA | Acadia Contractors | Unknown | NA | BGS asked to consult; advised to stop pulling carpet and have tiles tested
2022-11-01 | 7 Chimney Loop | IAQ Concerns | Owned | DEP Response Offices | 7 Chimney Ln | Augusta | Mold | Inspect areas requested by Jon Woodard | 2022-11-01 | 2022-11-10 | NA | NA | Servpro | Area successuflly remediated and cleaned. PMD asked to replaced lower walls that were removed
2022-11-01 | 264 Civic Ctr Dr | Storage Humidity | Leased | Basement Storage Area | 264 Civic Center Drive | Augusta | Mold | Inspect and advise regarding excess humidity in Storage Area | 2022-11-08 | NA | NA | NA | NA | SES advised DOL on humidity control; directed to consult Servpro for proper dehumidifiers to use
2022-11-03 | Blaine House | 2nd Floor Window Painting | Owned | 2nd Floor, several rooms | 192 State St | Augusta | Lead | Assess potential worker exposure to lead during painting | NA | 2022-11-18 | NA | NA | NA | Determined that workers will be safe (without PPE) during painting as-described in scope
2022-11-09 | MCC-Windham | Asbestos New Finding | Owned | Tunnel Walls | 17 Mallison Falls Rd | Windham | Asbestos | Test black mastic found on exterior fouondation walls of tunnels | NA | NA | AQM | 2022-11-14 | Envirovantage | All samples negative; results conveyed to remediation contractor and agency
2022-11-28 | MCC-Windham | Asbestos New Finding | Owned | Administration Security E and the Gymnasium | 17 Mallison Falls Rd | Windham | Asbestos | Test mastic found behind brick façade | NA | NA | AQM | 2022-12-05 | Envirovantage | All samples Positive; results conveyed to remediation contractor and agency
2022-11-28 | 19 Union St | Moldy Ceiling Tiles | Owned | Office of Cannabis Policy | 19 Union St | Augusta | Mold | Inspect several areas with water-stained / moldy ceiling tiles | 2022-11-29 | 12/2/22 (email) | NA | NA | BGS / PMD | SES Removed moldy ceiling tiles; PMD to replace
2022-11-28 | MFS, Bolton Hill HQ | Asbestos Flooring | Owned | Duty Room | 2870 North Belfast Ave | Augusta | Asbestos | Assess asbestos content for floor tiles in a small area where the tiles are damaged | NA | NA | AQM | 2022-12-08 | DEP | Only a very small area (a couple of tiles) was damaged and below regulatory level. Removed by DEP as a courtesy
2022-12-05 | 7 Chimney Loop | Ceiling Mold | Owned | DEP-Response Training Room | 7 Chimney Loop | Augusta | Mold | Determine cause of mold; provide remedial recommendations | 2023-01-10 | 2023-01-27 | NA | NA | Octagon | Ceiling previously tested by AQM. Ceiling cleaned by Octagon and re-painted by PMD
2022-12-09 | DOC-Lewiston | Particulate Issue | Leased | All 1st Floor DOC space | 198 Maine St, Suite A | Lewiston | IAQ / Particulates | Assess employee health issues and reports of particulates on office surfaces | 12/13/22, Multiple through Feb 2023 | 2023-01-05 | NA | NA | Octagon. Knowles Mechanical | Work surfaces detail-cleaned; HVAC cleaned; HVAC cabinet cleaned after fiberglass removal, remaining fiberglass encapsulated
2022-12-20 | Merrill-Smith | IAQ Test | Owned | Merrill (and common) Only, 1st and 2nd floor, not Attic or Basement | 187-189 State St | Augusta | IAQ & Mold | Pro-active test requested prior to occupancy | 2023-01-17 | NA | AQM | 2023-01-24 | PMD | AQM found only a dust issue; PMD was guided in cleaning practices and conducted the deep-cleaning

## 2023
Date Initiated | Building | Project | Owner / Leased | Department / Area | Street | City | Type | Scope of Work | Date BGS Onsite | BGS Rpt Date | OH&S Consultant Name | OH&S Consultant Rpt Date | Remediator Name | Outcome
2023-01-20 | Marquardt | 2nd Floor Sewer Odor | Owned | NRSC - South End / 2nd Floor | 32 Blossom Ln | Augusta | Odor | Determine Source of Sewer Odor | 2023-01-25 |  | NA | NA | PMD | PMD found and capped several open pipes
2023-01-31 | Elkins | 3rd Floor Roof Leak | Owned | 3rd Floor Hall by Rooms 314-319 | 19 Elkins Ln | Augusta | Mold | Determine water damage and cause of musty odor | 2023-02-01 | NA | NA | NA | PMD | Impacted walls are plaster and brick; only potential odor is from ceiling tiles, removed (2/1/23) by PMD
2023-01-27 | 1037 Forest Ave | Water Damage & Mold | Leased | Worker's Comp | 1037 Forest Ave | Portland | Mold | Advise Agency on recent water intrusion and presence / exposure to mold | NA | NA | AQM | 2023-01-28 | NA | Lessor was not cooperative; advised Agency through the process to break lease and reloacte
2023-02-05 | Marquardt | DMR Sprinkler Freeze | Owned | DMR, 2nd and 1st Floor | 32 Blossom Ln | Augusta | Dry-out | Coordinate material removal and dryout in timely manner | 2023-02-06 | NA | NA | NA | Servpro | Materials removed and remaining systems dried in timely manner to prevent mold growth (verification not necessary)
2023-02-05 | DHHS-Lewiston | Sprinkler Freeze | Leased | DHHS, Mezzanine and 1st Floor | 200 Main St | Lewiston | Dry-out | Assess water impact and mold potential; assign AQM for testing; Multiple inspections and testing required | 2023-02-09 | NA | AQM |  | Servpro (NJ) | Lessor eventually achieved satisfactory remediation state after several re-inspections and demads for compliance
2023-02-06 | Marquardt | Milk Lab Ice Maker Leak | Owned | Milk Lab (1st Floor) | 32 Blossom Ln | Augusta | Dry-out | Coordinate material removal and dryout in timely manner | NA | NA | NA | NA | Servpro | Materials removed and remaining systems dried in timely manner to prevent mold growth (verification not necessary)
2023-02-09 | MFS, Central Region HQ | Asbestos Flooring | Agency-Owned | All Flooring | 87 Airport Rd | Old Town | Asbestos | Assess flooring for asbestos content prior to renovations | NA | NA | AQM | 2023-02-21 | NA | Tiles to be removed are negative. Linoleum tested postitive but is not damaged and not planned for removal.
2023-02-14 | DHHS-Bangor | Roof Leaks | Leased | All Areas (sporadic locations) | 19 Maine Ave | Bangor | Dry-out | Assess areas of water impact and risk of mold | 2/17/2023, 3/3/23 | 2023-03-08 | NA | NA | NA | Most carpts and walls were dry. Micro exam of lower walls showed no mold. DHHS staff finished drying some lower walls.
2023-02-16 | MPUC-Hallowell | Groundwater | Leased | Crawlspace | 26 Katherine Dr | Hallowell | Mold | PUC concerned with possible electrical damage and mold growth in Crawlspace. Assess damage and work done by contractor hired by Lessor. | NA | NA | AQM | 2023-02-17 | Advance1 | Remediation done as recommended, clearance test passed.
2023-02-21 | State Police, Houlton Barracks | Asbestos Flooring | Owned | Emergency Communications office | 1 Darcie Dr # 202 | Houlton | Asbestos | Assess potential for damaged flooring to contain asbestos | NA | NA | NA | NA | NA | MPS provided original packaging for both the floor tiles and mastic; tiles marked as "No asbestos"; mastic asbestos-free based on current MSDS from manufacturer.
2023-02-23 | BMV-Scarborough | Roof-drain Leak | Leased | Station Area (central location) | 200 Expedition Dr | Scarborough | Mold | Assess area after drying and carpet replacement; also assess employee symptoms that occur when ceiling tiles are removed and ceiling left open | 2023-02-24 | NA | AQM | 2023-03-11 | Octagon | SES report issued requiring Lessor remediation (conducted and completed successfully). Additional employee concerns raised and assessed over several inspections. 2nd report issued requiring actions to address mold from long-term humidity and HVAC issues.
2023-02-28 | DHHS-Bangor | Exhaust Odor | Leased | All areas | 19 Maine Ave | Bangor | Odor | Apply ASHRAE standard to situation of aviation exhaust entrainment to HVAC, to force Lessor to pay for charcoal filters | NA | NA | NA | NA | NA | SES email to Lessor 3/31/23; Lessor responded immediately with intention to take care of charcoal filters
2023-03-07 | BVS SMVC Admin Building | Suicide | Owned | Men's Restroom | 83 Stanley Rd | Springvale | Bloodborne Pathogen | Coordinate cleaning and sanitation in response to suicide by firearm | NA | NA | NA | NA | Crime & Death Scene Cleaning | Some Restroom lower wall and floor materials removed, surfaces successfully cleaned.
2023-03-15 | Tyson | Window Lead Paint | Owned | All 3 Floors, along perimeter walls | 25 Tyson Dr | Augusta | Lead | Assess impact following accidental paint chip dislodging from windows during cleaning | 2023-03-16 | NA | NA | NA | Servpro | Servpro deep-cleaned heating units under widows and floor surrounding the heating units (all 3 floors)
2023-03-24 | State House | Room 410 Ventilation | Owned | Legislature / Room 410 | State House Station | Augusta | Ventilation | Assess occupant complaints of sleepiness and perceived, poor ventilaion | 2023-04-14 | 2023-04-21 | NA | NA | PMD | Inspection revealed flaws in air-supply to Room. SES advised PMD, who then modified the ducts to provide proper air supply
2023-04-04 | MFS-Outbuildings | MFS Outbuilding Lead Paint | Leased |  |  |  | Lead | Assess one or more outdoor vehicle storage bays for lead-based paint | NA | NA | NA | NA | NA | Project closed; agency request withdrawn
2023-04-07 | 221 State St | Asbestos | Owned | 1st Floor (Cubicle Area) Men's Restroom Closet | 221 State St | Augusta | Asbestos | Assess potential for asbestos in Closet | 2023-04-14 | 2023-04-14 | NA | NA | NA | No materials at risk for ACM except 2 boxes of stored 12x12 tiles, which were determined asbestos-free per manufacturer spec sheet
2023-04-12 | DEP Response | Room 141 Floor Tiles | Owned | DEP Response / Room 141 | 3 Chimney Loop | Augusta | Asbestos | Test floor tiles for asbestos (several loose tiles) | NA | NA | AQM | 2023-04-19 | NA | All samples were negative for asbestos - no actions required.
2023-05-01 | Deering | Roof Leak | Owner | DACF / Room 311 | 90 Blossom Ln | Augusta | Water Damage | Assess water impact from roof leak | 2023-05-02 | NA | NA | NA | NA | Only a very small wall area (several square inches) contained elevated moisture; advised employees to have custodian apply fan for another couple days.
2023-05-01 | Cross State Office Building | Roof Drain Leak | Owned | 6th Floor down to 1st Floor | 111 Sewall St | Augusta | Water Damage, Mold | Assess extent of water impact, dry areas / materials and remediate any mold | 2023-05-01 | NA | NA | NA | Servpro | Servpro removed walls and dried all areas possible; One column remained wet spanning 6th to 3rd floor. Servpro removed column walls and associated mold under containment
2023-05-01 | Lamoine Barn | Roof Leaks | Owned | DMR / Offices | 22 Coaling Station Lane | Lamoine | Water Damage, Mold | Assess impact to building and employees and provide recommendations for remediation | NA | NA | AQM | 2023-05-15 |  | Assessment conducted by AQM and report issued to Agency (advised to avoid use of impacted areas). Remediation on hold pending building engineering assessment
2023-05-02 | DEP Tech Services Garage | Roof Renovation | Owned | Exterior / Roof | 174 Hogan Rd | Bangor | Asbestos | Test roof shingles for asbestos prior to renovation | NA | NA | AQM | 2023-05-15 | NA | Asbestos is not present in roofing materials
2023-05-02 | Cross State Office Building | Window Leak | Owned | Attorney General / 7th Floor Room 748 | 111 Sewall St | Augusta | Water Damage, Mold | Assess impact from window leak | 2023-05-19 |  |  |  |  | Chronic damage to sheetrock surrounding window. Mold growth possible within wall cavity (no exposed mold). Remediation on hold until façade work complete (to prevent further water intrustion)
2023-05-03 | Greenlaw | Window Leaks | Owned | 1st Floor, 3rd Floor | 47 Independence Dr | Augusta | Water Damage | Assess water impact from window leaks in 2 locations | 2023-05-08 | 2023-05-09 | NA | NA | NA | All walls dry within 2 weeks with no visible mold. Determined wallboard is mold resistant. Test cut made in 1 wall (1st Floor) and mold growth not present on backside of wallboard
2023-05-04 | 286 Water St / Key Plaza | 4th Floor Water Infiltration | Leased | DHHS / 4th Floor NE Corner | 286 Water St | Augusta | Water Damage, Mold | Assess water impact to rooms in the NE corner | 2023-05-04 | 2023-05-04 | AQM | 2023-06-12 | Lessor | SES report issued with recommendations. AQM also tested and provide report. Lessor used Servpro to remediate. Clearance testing passed.
2023-05-04 | DHHS-Machias | Mold May2023 | Leased | BCFS area of the building | 38 Prescott Drive | Machias | Mold | Assess employee reports of health issues and water damage, and suspected mold in carpet | NA | NA | AQM | 2023-06-16 | Eastern Mold Remediation | AQM Inspected and provided report to address mold. Lessor addressed issues. Clearnace test passed
2023-05-09 | Blaine House | Garage Painting | Owned | Garage | 192 State St | Augusta | Lead | Coordinate surface-prep and repaining (current paint is lead-based) | NA | NA | NA | NA | Servpro | SES consulted with several potential contractors and chose Servpro to remove loose paint and dust and to repaint. Project scheduled for early spring 2024.
2023-05-25 | MPUC-Hallowell | IAQ Test | Leased | All areas / floors | 26 Katherine Dr | Hallowell | IAQ | Assess IAQ to address employee reports / concerns | NA | NA | AQM | 2023-06-15 | NA | IAQ Testing found no significant issues. SES met with Agency to explain results
2023-05-31 | CDS-Arundel | Preschool Water Dmg | Leased | Preschool Wing | 39 Limerick Rd | Arundel | Water Damage / Mold | Assess area for water impact and potential mold. | 2023-06-08 | 2023-06-21 | NA | NA | Unknown | SES identified mold on some walls from past toilet overflow and mold in HVAC from humidity. Report sent to Lessor. Agency reported that Lessor addressed areas via a certified contractor and were satisified with the work
2023-06-01 | Cultural Building | Mold May2023 | Owned | Museum / 4th Floor Small Temp Gallery | 230 State St | Augusta | ME | Assess water impact caused by Abatement Contractor on 5th Floor | 2023-06-02 | 2023-06-06 | NA | NA | Octagon | SES identified wet walls and mold in impacted areas on both floors. General Contractor for the larger, ongoing building project oversaw remediation. Clearance test passed
2023-06-07 | Marquardt | Room 377 Odor | Owned | DEP / Room 377 (north) | 32 Blossom Ln | Augusta | ME | Assess employee report of musty odor in the room | 2023-06-14 | NA | NA | NA | NA | There were no water-damage or mold issues found (SES inspection)
2023-06-08 | DACF-Jonesboro Office | Roof Renovation | Owned | Roof (back side) | 307 Whitneyville Rd | Jonesboro | ME | Sample the roof for ACM prior to renovation | NA | NA | AQM | 2023-07-05 | NA | Materials tested in the House and garage all tested negative for asbestos
2023-06-14 | F Building (DDPC) | Musty Odor | Owned | DOC / 2nd Floor | 102 Hogan Rd | Bangor | ME | Assess area of complaint for mold / musty odor | 2023-06-27 | 2023-06-30 | NA | NA | Unknown | SES inspection identified wet and moldy wall and flooring from plumbing leak. Report issued and handled by Lessor. Agency reported satisfactory resolution
2023-06-28 | BMV Main Office | Musty Odor | Owned | BMV / License Information | 101 Hospital St | Augusta | Mold | Assess area of complaint for mold / musty odor | 2023-06-29 | 2023-06-30 | AQM | 2023-08-02 | Servpro | SES identified mold on air-supply diffusers. AQM testing found no airborne mold concerns. Servpro cleaned all diffusers and employee work areas
2023-07-07 | Briggs Hall / Bldg A | FATS Humidity Mold | Owned | FATS Room (A004) | 15 Oak Grove Rd | Augusta | Mold | Assess musty odors and mold on ceiling tiles | 2023-07-18 | 2023-07-20 | NA | NA | Servpro | Mold growth from humidity identified on most surfaces. Servpro removed ceiling tiles and deep-cleaned all areas.
2023-07-11 | DOC-Ellsworth | Building Assessment | Leased | All DOC areas | 412 High St | Ellsworth | HazMat | Assess general employee concerns for visible damage in some areas and assess building prior to new lease | NA | NA | AQM | 2023-09-10 | NA | DOC chose to break lease and relocate due to the extent of water and mold-related damages
2023-07-17 | Crime Lab | DNA Lab Humidity | Owned | DNA Lab | 36 Hospital St | Augusta | Mold / Water Damage | Assess condensation above ceiling and moldy ceiling tiles | 2023-07-18 | 2023-07-21 | AQM | 2023-07-21 | Servpro | SES report issued. Servpro deep-cleaned all impacted areas. Clearance test passed. Dehumidifier installed
2023-07-17 | Ray Bldg | Humidity Mold | Owned | Ground Level | 28 Tyson Dr | Augusta | Mold | Assess cause of mold growth on lower walls during renovation | 2023-07-20 | 2023-07-24 | NA | NA | Benchmark | Contractor (Benchmark) removed moldy sheetrock; SES advised on how to control humidity during renovation
2023-07-18 | OCME | Conference Room Ceiling Mold | Owned | OCME / Conference Rm (Ground Lvl) | 30 Hospital St | Augusta | Mold | Assess mold growth on ceiling tile in Conference Rm | 2023-07-25 | 7/28/23 (email) | NA | NA | NA | Ceiling tile removed prior to SES inspection. Details of plumbing leak sent to PMD
2023-07-24 | MSL-Winthrop Warehouse | Winthrop Warehouse Dust | Leased | MSL Winthrop Warehouse, Storage Area | 1705 Route 202 Suite #1 | Winthrop | IAQ | Assess employee complaint of dust and hazardous work environment | 2023-07-26 | 7/28/23 (email) | NA | NA | Octagon | SES determined that the situations is not "hazardous" and there is common dust accumulation. Recommended general cleaner
2023-07-25 | DHHS-Lewiston | Stockroom Odor | Leased | Stockroom (1st Floor) | 200 Main St | Lewiston | Odor | Assess cause of odor | 2023-08-03 | 8/3/23 (email) | NA | NA | NA | Odor determined to be related to new flooring installed by Lessor. Agency advised to ventilate the area to dissipate odor over time
2023-07-26 | 35 Anthony Ave | Atrium Ceiling Leak | Leased | Atrium | 35 Anthony Ave | Augusta | Mold | Assess extent of mold resulting from roof leak. | 2023-07-26 | 7/23/23 (email) | AQM | 8/2/23 (Lab Results | Servpro | Servpro remediated the impacted areas. Clearance test passed
2023-08-02 | CDS-Ellsworth | Mold Concerns | Leased | EIPM Office | 190 Bangor Rd | Ellsworth | Mold | Employees are concerned about possibly mold on a window sash; there are other non-mold complaints also | NA | NA | AQM | 9/17/23, 11/5/23 | Unknown | AQM Inspected and provided report to address mold. Lessor did not follow recommendations. Follow-up report found several deficiencies. Agency broke lease and relocated
2023-08-03 | 109 Capitol St | IAQ | Leased | DHHS / Commissioner's Finance | 109 Capitol St | Augusta | IAQ | Assess employee complaint of allergy reaction | 2023-08-11 | 2023-08-21 | NA | NA | NA | SES inspection identified some very dusty work surfaces including a fan previously located elsewhere (dust contained fiberglass). Advised removal of fan and cleaning of dust
2023-08-08 | Tyson | Room 324 Odor | Owned | DOC / Room 324 | 25 Tyson Dr | Augusta | Odor | Assess cause of odor | 2023-08-09 | 2023-08-17 | NA | NA | NA | SES inspection identified cluttered and dusty conditions and complete lack of ventilation (door is kept closed). Advised cleaning and adding vent to door
2023-08-08 | Hospital St Fire Station | Tennis Courts HazMat | Owned | Tennis Courts | 40 Hospital St | Augusta | Asbestos, Lead | Assess tennis courts for lead and asbestos prior to demolition | 2023-08-11 | NA | AQM | 8/18/23 (Lab Results) | NA | No lead or asbestos found
2023-08-09 | Gov Baxter School for the Deaf Building-D | Mold / Water Damage | Owned | Ground Level and 1st Floor | Mackworth Island | Falmouth | Mold | Assess cause and extent of mold | 2023-08-16 | 2023-08-24 | NTC | 2023-07-26 | Unknown | SES inspection identified mold on furniture, some lower walls and remaining carpet. GBSD removed all carpet and furniture and is managing the remediation
2023-08-15 | MFS Ranger Station, Benton | Basement Mold | Owned | Basement Level, all areas | 57 Bangor Rd | Benton | Mold | Assess water damage and mold in Basement | 2023-08-18 | 2023-08-25 | NA | NA | Servpro | SES inspection identified mold due to humidity and groundwater. Servpro to address in early 2024.
2023-08-16 | DEP-Portland | Carpet Mold | Leased | DEP (multiple areas) | 312 Canco Rd | Portland | Mold | Test carpet for mold growth on one area of suspicion | 2023-08-29 | 2023-09-08 | Sevee & Mahar | Unknown | Envirovantage | SES inspection found no mold in carpets but found wet lower walls and mold growth along perimeter walls. Report issued to Lessor who is using his IEP and remediation firm to address the issues
2023-08-23 | DHHS-Lewiston | Roof Leak | Leased | Fraud / 2nd Floor | 198 Main St | Lewiston | Water damage | Identify wet materials and advise on drying | 2023-08-24 | NA | NA | NA | NA | SES identified several small areas of wet walls. DHHS Staff dried walls using fans (verified with moisture meter)
2023-08-28 | Nash School | Musty Odor | Owned | Basement |  | Augusta | Mold | SES inspection identified mold growth in basment due to humidity and groundwater | 9/5/23, 9/12/23 | 2023-09-28 | NA | NA |  | SES inspection identified mold due to excess humidity. Report issued with recommendations. Remediation on hold pending overhall of entire building. Dehumidifiers in basement stopped odors.
2023-08-30 | Cross State Office Building | 6th Floor Roof Leaks | Owned | 6th Floor - Attorney General Area | 111 Sewall St | Augusta | Water Damage | Assess impact from water intrusion due to heavy rain | 2023-08-30 | 2023-08-30 | NA | NA | Servpro | Servpro removed some walls and dried materials and carpets. Removed (under containment) minor areas of mold on lower walls. Rebuilding awaiting fix for roof
2023-08-31 | Blaine House | Living Room Mold on Wall | Owned | Living Room wall facing the New England Garden | 192 State St | Augusta | Mold | Assess mold on wall | 2023-08-31 | 2023-09-01 | NA | NA | NA | Mold on wall determined to be superficial and formed from humidity eminating from wall and light fixture. Source determined to be basement. Advised placement of dehumidifiers in basement and controlling rainwater runoff
2023-09-05 | Tyson | Musty Odors | Owned | 3rd Floor |  | Augusta | Mold | Assess source of musty odors and wet ceiling tiles | 2023-09-07 | 2023-09-08 | NA | NA | NA | SES identified several water leaks and points of condensation above ceiling tiles. Leaks were addressed and ceiling tiles replaced
2023-09-11 | State House | Library Mold | Owned | Law Library |  | Augusta | Mold | Assess report of mold suspected on on wall AC units located on perimeter wall | 2023-09-12 | 2023-09-12 | NA | NA | Servpro | SES identified mold growth in most of the AC units and on bookshelves in 1 corner of the room, all due to humidity. Servpro deep-cleaned to remove mold
2023-09-19 | 221 State St | Unknown Liquid | Owned | HETL, Basement Rm 106 and adjoining areas | 221 State St | Augusta | Chemical / Unknown | Assess dark liquid leaking from HVAC ducts | 2023-09-20 | 2023-09-21 | NA | NA | NA | SES inspection determined that liquid was due to condensation inside ducts and old dust impacted by acid vapor (giving the dark color). Advised HETL that cleaning with standard, minimal precautions (PPE) is acceptable
2023-10-11 | MCJA, Building-A | Basement Office Expansion | Owned | Basement, 2 rooms next to Evidence Storage Room | 15 Oak Grove Rd | Vassalboro | Pro-active Inspection | Assess suitabality of rooms for uses as offices | 2023-10-18 | 2023-11-02 | NA | NA |  | SES identified several mold and wall-damage issues and discovered substantial mold growth in the Evidence Storage. Intended office use was abandoned. Mold remediation awaiting decision on relocation of evidence storage
2023-10-16 | 353 Water St | Carpet Mold | Leased | Unknown Area | 353 Water St | Augusta | Mold & Bacteria | Servpro requesed advice for carpet impacted by water and with strong sour odor | NA | NA | NA | NA | Servpro | Remediation managed by Lessor; After several unsuccessful cleaning attempts, the carpet was replaced
2023-10-19 | Greenlaw | Neutralization Sump Gases | Owned | Sample Neutralization (Room 128) | 47 Independence Dr | Augusta | Odor / Chemical | Employees concerned about possible airborne exposure to gases / chemicals | 2023-10-20 | 2023-10-20 | NA | NA | NA | SES determined that odors are from (minor) general / non-specific volatile compunds eminated from a poorly sealed sump pit. Advised HETL to seal the cover or provide aggressive exhaust ventilation
2023-10-23 | DOC-Auburn | Ceiling Mold | Leased | 2nd Floor, 1 room | 5 Burns St | Auburn | Mold | Assess mold growth on ceiling | 2023-10-24 | 2023-10-30 | NA | NA | Service Master | SES inspection conducted; report with remediation scope provided to Lessor. Successful remediation by Service Master
2023-10-23 | Gardiner Annex | IAQ Concern | Leased | Unknown, 1 cubicle area (1 employee) | 76 Northern Ave | Gardiner | IAQ & Mold | Conduct testing to address employee concerns | 2023-10-30 | NA | AQM | 2023-11-06 | NA | Testing by AQM identified normal conditions; mold growth not present on items of concern to employee
2023-10-23 | Gardiner Annex | BFI Examiner Roof Leak | Leased | BFI Examiner Area | 76 Northern Ave | Gardiner | Water Damage | Assess impact from ceiling leak | 2023-10-30 | NA | NA | NA | NA | Water impact was predominantly to a table, only a very small area of carpet was wet. Drying fan set up and dried over next several days
2023-10-30 | CDS-Portland | Mold & Water Damage | Leased | Unknown Area | 1011 Forest Ave | Portland | Water Damage / Mold | SES asked to assist Leased Space in guiding Lessor to the required remediation and documentation | NA | NA | NA | NA | NA | Project is ongoing and being directed by the Lessor. SES will assist Leased Space as needed.
2023-11-03 | Hospital St Fire Station | Abatement Oversight | Owned | Unknown Area | 40 Hospital St | Augusta | Asbestos | SES was asked by PDC to provide 3rd party assessment of abatement contractor's work | NA | NA | AQM | 2023-11-13 | Unknown | AQM identified several deficiencies in protocol and equipment. After several re-inspections, contractor was cleared to begin
2023-11-06 | Gardiner Annex | Water Cooler Mold | Leased | OPOR | 76 Northern Ave | Gardiner | Mold | Assess areas where water coolers had been installed | 2023-11-09 | 2023-11-16 | NA | NA | Servpro | Signs of leakage found in 2 of 8 locations, 1 of which contained mold growth. Informed Lessor, who used Servpro to successfully remediate
2023-11-17 | BMV-Scarborough | Mold | Leased | All Areas | 200 Expedition Dr | Scarborough | Mold | Project re-opened by BMV. Assisted with 3rd-party mold inspection. Identified several areas with definitive issues. Demand for remediation will be sent to Lessor | 2023-12-06 | NA | AQM |  |  | SES in conjunction with AQM identified mold issues related to humidity and a ceiling leak. A report will be issued to Lessor requiring remediation.
2023-11-20 | Vital Records | IAQ | Owned | All Areas | 220 Capitol St | Augusta | IAQ | Conduct IAQ sampling in response to employee inquiry of any recent testing | 2023-11-22 | 2023-12-01 | NA | NA | NA | SES testing found all IAQ parameters to be within normal ranges except for low humidity, which is common in winter
2023-11-21 | Cross State Office Building | Dep. Commissioner's Office IAQ | Owned | 4th Floor, Office of 1 employee | 111 Sewall St | Augusta | IAQ | Assess office for anything that could affect health | 2023-11-21 | 2023-12-01 | NA | NA | BGS | Identified dusty conditions. Found disporportionate amount of mold and starch in dust. Relocating printers to address starch. Assessing HVAC system to address mold
2023-11-27 | 45 Commerce Dr | IAQ | Owned | SESC - Human Resources Office | 45 Commerce Dr | Augusta | IAQ | Assess employee work areas for anything that could affect health | 2023-11-30 | 2023-12-22 | NA | NA | NA | Found all IAQ parameters to be within normal ranges except for low humidity, which is common in winter. Work areas were very dusty. Dust contained normal components. Report issued to address cleaning and dust
2023-11-30 | 85 Leighton Rd | Rodent Issue | Leased | OIT Print Room | 85 Leighton Rd | Augusta | Rodent | OIT reported foul odors and dead rodents in Print Room. SES inspected and provided recommendations for cleaning | 2023-11-30 | 2023-12-01 | NA | NA | Service Master | Service Master cleaning conducted in timely manner to avoid shut-down of print operations
2023-12-04 | State House | Radon Assessment | Owned | All Areas | State House Station | Augusta | Radon | Assess building for radon per State and Federal standards | 2023-12-11 | NA | Goodwin Environmental |  |  | Ongoing
2023-12-05 | Cross State Office Building | Commissioner's Office IAQ | Owned | 3rd Floor, Office of 1 employee | 111 Sewall St | Augusta | IAQ | Assess office for anything that could affect health | 2023-12-15 |  |  |  |  | Ongoing
2023-12-06 | Hospital St Fire Station | Transite Pipe | Owned | Outdoors (underground) | 40 Hospital St | Augusta | Asbestos | Apply DEP regulations and provide 3rd-Party testing | NA | NA | AQM | 2023-12-12 | Unknown | Consultation with DEP indicated the ise issue was not a regulated item. Testing confirmed asbestos. Contractor is free to properly remove the pipe

## 2024
Date Initiated | Building | Project | Owner / Leased | Department / Area | Street | City | Type | Scope of Work | Date BGS Onsite | BGS Rpt Date | OH&S Consultant Name | OH&S Consultant Rpt Date | Remediator Name | Outcome
2024-01-26 | DOL-Bangor | Mold Complaint | Leased | EMDC | 45 Oak St | Bangor | Mold | Assess area of concern for water damage and mold | 2024-02-08 | 2024-02-20 | NA | NA | NA | SES inspection found no water damage or mold issues except water-stained carpet (Microscopic exam indicated no mold in carpet)
2024-02-08 | DOL-Presque Isle | Allergy Reaction | Leased |  | 66 Spruce St | Presque Isle | Allergy | Assess and test area of concern for potential allergens including mold | NA | NA | AQM | 2024-03-17
2024-02-09 | Smith Bldg | Water Damage | Owned | 1st and 2nd Floor at Conference Rm | 187 State St | Augusta | Water Damage | Assess water damage for potential mold | 2024-02-14 | NA | AQM | 2024-02-28 | NA | Only minor ceiling stains. Air samples requested for mold. No concerns identified in sample results.
2024-02-13 | 10 Water St | Ceiling Mold | Owned | History Storage Room | 10 Water St | Hallowell | Mold | Assess ceiling for mold growth | 2024-02-16 | NA | NA | NA | Octagon | Minor mold growth found on ceiling close to perimeter wall, due to humidity and item stacking. Octagon cleaned, mold removed
2024-02-26 | BMV-Augusta | HVAC Mold | Owned | Finance Office | 101 Hospital St | Augusta | Odor / Mold | Assess musty odor and particulates on work surfaces | 2024-02-28 | 3/15, 3/21 (photo & email)
2024-03-04 | AG Office, Caribou | Ceiling Leaks | Leased | Space leased by OMAG | 14 Access Highway | Caribou | Water Damage | Assess water-impacted ceiling insulation for mold | NA | NA | AQM | 2024-03-26 | NA | No mold growth or airborne mold found in areas of concern. Minor mold in attic - Lessor asked to address / replace roof sheathing
2024-03-21 | AG Office, Portland | Musty Odor | Leased | Space leased by OMAG | 125 Presumpscot St | Portland | Odor / Mold | Assess transient musty odors in areas or prior water infiltration | 2024-04-03