02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

174		BOARD OF BOILERS AND PRESSURE VESSELS

# Chapter 12:	POWER BOILERS

SUMMARY: This Chapter establishes requirements for the design, construction, installation, operation, and inspection of power boilers.

# 1.	New Installations

# A.	Approval of Installation. Before a power boiler is installed, the owner must submit to the Chief Inspector detailed plans and specifications of the installation for approval at least 30 days prior to installation on a form provided by the Board. The owner must comply with any request by the Chief Inspector for additional information. A power boiler may not be installed unless the Chief Inspector has issued a written approval for the installation. Emergency situations will be handled on a case by case basis by contacting the Chief Inspector.

# B.	Initial Inspections

(1)	Inspection. The Chief Inspector shall conduct the initial inspection of a new or relocated power boiler in accordance with the applicable code(s) specified in Chapter 11 of these rules. The initial inspection must consist of an internal and external inspection, if construction permits. Additionally, a hydrostatic test must be completed of the entire boiler and boiler external piping after field installation. The Chief Inspector shall record and submit the results of the inspection to the Board.

(2)	Interim Inspection Certificate. If after initial inspection the Chief Inspector determines that a power boiler complies with all provisions of Title 32, Chapter 131, the Board’s rules, and the applicable national code(s), the Chief Inspector may issue an interim inspection certificate for the operation of the power boiler up to 60 days pending issuance of the initial inspection certificate.

(3)	Expenses. The owner or the owner’s designee must pay the initial inspection fee and any related expenses for the initial inspection of a power boiler. If the fee has not been paid by the date the interim certificate expires, the Chief Inspector shall direct the owner to suspend operation of the power boiler.

# C.	Approval of Operation. Before a newly installed power boiler is operated, the owner must comply with the provisions of Paragraphs A and B, and the Chief Inspector must approve the operation on a form provided by the Board.

# D.	Relocation. Before a relocated power boiler is installed, the owner must petition the Chief Inspector for a variance to approve the installation. A relocated boiler must meet the requirements for new installations, where practicable.

# 2.	Existing Power Boilers

A.	Rules Applicable to Construction and Installation. The design, construction, construction-related inspection, installation, and stamping of all existing power boilers must comply with the rules of the Board in effect at the time of installation.

B.	Rules Applicable after Installation. The maintenance, operation, and post-installation inspection of all existing power boilers must comply with the rules of the Board in effect at the time of the maintenance, operation, or post-installation inspection.

# 3.	Registration Numbers

A.	Display; Not Transferable. The assigned State of Maine registration number must appear on each power boiler at all times. The registration number assigned to a power boiler may not be transferred to another boiler.

B.	High Pressure Numbers. Before any power boiler may be operated in this State, the assigned State of Maine registration number preceded by the letters “ME” must be stamped on the power boiler with the numbers and letters not less than 3/8 of an inch in height. The stamp must appear in the vicinity of the manufacturer’s code stamping.

# 4.	Periodic Inspections of Power Boilers

A.	Frequency and Method. Before the initial inspection certificate expires, and annually thereafter, all power boilers in the State must be inspected as follows: an Inspector must conduct 1 annual certificate inspection, which must be an internal inspection, and 1 annual external inspection conducted approximately 6 months from the date of the certificate inspection while the boiler is in operation. Miniature boilers must receive a certificate inspection once every year and an internal inspection once every 2 years. The external inspection must be documented by the Authorized Inspector on the inspection certificate.

B.	Report. An Inspector must submit a report of each certificate inspection required under Paragraph A to the Board on a form approved by the Board.

5.	MAWP of Existing Power Boilers Not Constructed to Code

The MAWP on the shell of a power boiler or drum shall be determined by the strength of the weakest course computed from the thickness of the plate, the tensile strength of the plate, the efficiency of the longitudinal joint, the inside diameter of the course, and the factor of safety allowed by Paragraph A. The formula for determining MAWP is as follows:

# TStE = MAWP, PSIG

RFS

# Where:

TS	= 	Ultimate tensile strength of shell plates, PSI

R	= 	Inside radius of the weakest course of the shell or drum, inches.

t	= 	Minimum thickness of shell plates in weakest course, inches.

E	= 	Efficiency of longitudinal joint, as calculated in the ASME Boiler and Pressure Vessel Code specified in Chapter 11 of the Board’s rules.

FS 	= 	Factor of Safety allowed by Paragraph A.

A.	Factor of Safety. The factor of safety must be at least 5.

B.	Tensile Strength. When the tensile strength of steel or wrought-iron shell plates is not known, it must be assumed to be 55,000 PSI for steel and 45,000 PSI for wrought iron.

C.	Strength of Rivets. Calculations concerning riveted joints must be those established by the ASME Boiler and Pressure Vessel Code specified in Chapter 11 of these rules, or as approved by the Board.

# 6.	Lap Seam Boilers

No boiler of longitudinal lap seam construction may be installed or operated as a power boiler within the State.

# 7.	Non-Code H.R.T. Boilers

A non-code horizontal return tubular boiler may not be installed or operated as a power boiler unless it was in use in this State before January 9, 1936.

# 8.	Pitch Horizontal Firetube Boilers

Horizontal firetube boilers must be pitched toward the blow-off outlet not less than 1 inch for each 10 feet of tube length when set.

# 9.	Manual Dampers

Fully closable manual dampers are prohibited on automatically fired power boilers. The owner must ensure that any such existing dampers are removed.

10.	Engineers-in-Charge

The owner must assign an engineer-in-charge for any power boiler operated in the State of Maine. The engineer-in-charge must comply with the provisions of Chapter 32, Section 7 of these rules.

# AUTHORITY: 	32 MRSA § 15104-A(1)

# REPEALED AND REPLACED:

# January 15, 2005 -	filing 2005-22 repealed old Chapter 12

# filing 2005-23 adopted new Chapter 12